## Slide 1: High Voltage Capacitor Discharge Tool
Group 14
Sponsored by NextEra Energy

## Slide 2: The Team
Electrical Engineering
Electrical Engineering
Computer Engineering
Electrical Engineering
Javier Lopez-Marrero
Will Serface
Kealan Frost
Zeeshan Asif

## Slide 3: Table of contents 01 04 02 05 03 06
Background & Administration
System Design & Hardware Selection
Schematics & PCB Layouts
Software Design
Prototyping & Testing
Future Plans

## Slide 4: Background & Administration 01

## Slide 5: Motivation and Background
NextEra uses capacitor banks for their inverters
Safety is a big concern with high amounts of voltage and risk of electric shock and potential system breakdown.
NextEra has tasked the team with designing a capacitor bank discharge tool prototype.

## Slide 6: Goals and Objectives
Designed System Should Be:
Safe & Reliable
Quick
User-friendly
Configurable
Scalable
This Led to the Following Objectives:
Implement 3 controllable, resistive discharge stages
Discharge capacitor in < 30 secs
Provide 4 status indications
Provide 4 configurable setpoints
Scale system to support 1200V
Notes: Clarify testing only at 12V

## Slide 7: Engineering Specifications
Critical Design Specifications:
Discharge time <= 30 seconds
3 Stage discharge
Stage voltage setpoints
Prototype Levels:
High voltage design (1200V nominal, 1500V max)
Low voltage design (12V nominal, 15V max)

## Slide 8: Work Distribution and Flow
Subsystem | Primary | Secondary | Responsibilities
Sensing and Isolation | Kealan Frost | Will Serface | Sensor research and selections
 |  |  | Sensor circuit designs
 |  |  | Sensor, MCU, and relay integration
 |  |  | Isolation from high voltage
Discharge | Javier Lopez-Marrero | Kealan Frost | Power resistor research and selection
 |  |  | Relay research and selection
 |  |  | Discharge network design
 |  |  | Relay and MCU integration
Computing | Will Serface | Zeeshan Asif | MCU research and selection
 |  |  | Display and I/O research and selection
 |  |  | Embedded Programming
 |  |  | User interface design
Power | Zeeshan Asif | Javier Lopez-Marrero | External power research and selection
 |  |  | Regulator designs
 |  |  | Capacitor charging circuit design
 |  |  | Chassis grounding
Team Meets 2-3x a Week
PCB Design Work is Collaborative
Manufacturing/Testing is also Collaborative

## Slide 9: Initial Budget

## Slide 10: 02 System Design & Hardware Selection

## Slide 11: Hardware Block Diagram
Notes: Add USB connection/Programming (Done)

## Slide 12: System CAD
Main PCB
I/O PCB
Display
Power
Relays and Contactors
24’’
12’’
6’’
Notes: Add Tags for Things (Done)

## Slide 13: Power Resistor Selection
Key Factors in Selection Included:
Voltage and Power Handling Ability
Product Availability / Resistance Value Availability
Overall Size and Mounting Style
Cost

## Slide 14: Relay Selection
Key Factors in Selection Included:
Switching/Contact Voltage and Carry/Load Current
Coil Characteristics (Voltage and Current)
Typical Lifetime (Mechanical/Electrical)
Cost

## Slide 15: Configuration of Discharge Stages
Max Discharge Time: ~24 secs
Min Discharge Time: ~18 secs
Energy/Power Dissipated: 1188 J / 49.5 W
Stage 1 Resistance: 10k
Stage 2 Resistance: 4.7k
Stage 3 Resistance: 1.88k

## Slide 16: Isolation Hardware Technology
Technology | Use | Accuracy | Simplicity
Analog Isolation | Copying analog signals across boundary | High | High
Digital Isolation | Transferring digital signals across boundary | Very High | Low
Device | Input Range | Isolation Rating | Integration Complexity
ADUM3195BRQZ | Op amp input | 3000 Vrms | Very High
AMC3330Q1 | +/- 1V | 4250 Vrms | Low
AMC1301DWVR | +/- 250mV | 5000 Vrms | High
Key factors:
Design complexity and robustness
Device input range, isolation rating, and supporting component complexity

## Slide 17: Temperature Sensing Technology
Technology | RTD | NTC | Thermocouple | Analog IC | Digital IC | IR non-contact
Sensing Range | -50 to 250 C | -40 to 125 C | 0 to 800 C | -40 to 125C | -40 to 125C | -70 to 350 C
Accuracy | +/- 0.3 to 0.8 C | +/- 0.5 to 2 C | +/- 1.1 to 2.2 C | +/- 0.5 to 2 C | +/- 0.5 C | +/- 0.5 C
Linearity | High | Nonlinear | Nonlinear | Medium | Medium | Nonlinear
Cost | Medium-High | Low | Medium | Low | Low | High
Integration Effort | Medium | Low | High | Very Low | Low | High
Key factors:
Temperature sensing range
Integration effort / linearity

## Slide 18: Temperature Sensing Component
Device | MAX31865AAP+ | LTC2983HLX | ADS1248IPWR
Type & Channels | Dedicated RTC-digital converter, 1 channel | Multi temp sensor input system, 20 inputs | General sensor input system, 8 channels
Integration Complexity | Very Low | Medium | High
Key factors:
Required external circuitry / integration complexity

## Slide 19: Microcontroller Technology
 | Arduino | ESP32 | STM32
Familiarity | Medium | Low | Medium
Compatibility | High | Medium | Low
Power | Medium | High | Low
Speed | Medium | High | Medium
I/O | Low | Medium | High
Key Factors:
  Availability of documentation and supporting libraries
  Product knowledge and support from Dr. Weeks

## Slide 20: Microcontroller Selection
ESP32 Model | WROOM-32D | C3FH4AZ
GPIO Pins | 32 | 16
CPU Frequency | 240 MHz | 160 MHz
RAM | 520 kB | 400 kB
Flash Storage | 4 MB | 4 MB
Architecture | Xtensa RISC-V | RISC-V
Key Factors:
  Availability of documentation and supporting libraries
  Product knowledge and support from Dr. Weeks

## Slide 21: User Interface Technology
 | Liquid Crystal | E-Ink | Segmented
GPIO Required | Low to Medium | Medium | High
Visibility | Medium | High | High
Versatility | High | High | Low
Information Density | High | Medium | Low
Key Factors:
  Ability to convey changing types of data to users at various distances
  Physical controls for PPE-wearing users

## Slide 22: User Interface Selection
Display Models | KD50G21-40NT-A1 | NHD-5.0-800480FT | GDEY042T81
Screen Size | 5” | 5” | 4.2”
Resolution | 800x400 | 800x480 | 400x300
Coprocessor | None | FDTI FT812Q | STM32
Color Space | sRGB | sRGB | B&W
Interface | 24-bit Parallel | SPI | SPI
Key Factors:
  Ability to convey changing types of data to users at various distances
  Physical controls for PPE-wearing users

## Slide 23: Power Table
Component level power estimates guided power supply selection.
The total current estimation from the 3.3- and 5-volt rails was evaluated to choose serviceable regulators
Component | Maximum Current Required | Voltage Required | Quantity | Maximum Power Consumption
Isolation Amplifier | 48 mA | 5V | 1 | 240 mW
Dual Operational Amplifier | 15 mA | 5V | 2 | 150 mW
General Voltage Reference | 50 mA | 5V | 1 | 250 mW
Relays | 85 mA | 24V | 3 | 6.12 W
Transistor | 20 mA | 3.3 V | 3 | 199 mW
RTD to Digital | 3.5 mA | 3.3V | 1 | 11.5 mW
MCU | 50 mA | 3.3V | 1 | 165 mW
Display | 100 mA | 3.3V | 1 | 330 mW
LED’s | 20 mA | 3.3V | 4 | 26.4 mW
Current limiting resistors for buttons | 40 mA | 3.3 V | 3 | 396 mW
3.3- and 5-volt regulators | 3 A(for both) | 3.3 V/5V | 2(1 of each) | 5V- 274 mW 3.3V- 1.414 W
Display driver | 590 mA | 3.3V | 1 | 1.947 W
Total Current Consumption (3.3 V) | 980 mA |  |  | 
Total Current Consumption (5 V) | 128 mA |  |  | 
Total Power Consumption | - | - | - | 11.52 W

## Slide 24: Power Supply Selection
Several power supply options available
Factors of consideration
Earth ground/proper grounding
Mounting adaptability
Enclosure safety
Adapter | MPE100C | RWS50B-24 TDK | Mean Well RPS-200 | NUOWEIDE | PMT-24V100W2BA
Wattage | 100 W | 50 W | 200 W | 600 W | 100 W
Current capability | 0-4.5A | 0-2.2A | 0-5.9A | 0-25A | 0-4.5A
Voltage capability | 85-264 VAC | 100-240 VAC | 80-264 VAC | 110-220 VAC | 90-260 VAC
Efficiency | 90% | 87% | 94% | 90% | 90%
Price | $52.74 | $37.17 | $46.00 | $29.99 | $23.93

## Slide 25: Regulator Selection
Voltage stepped down so buck converter is the best option
Factors for selection
Switching frequency
Load Current
Thermal performance
PCB construction
Category | LM 2576 | LM 2575 | LM 2596 | LM 2678 | TPS 5430
Maximum Output Current | 3 A | 1 A | 3 A | 5 A | 3-4 A
Input voltage range | 4-40 V | 4.75-40 V | 4.5-40V | 8-40V | 5.5-36V
Output voltage range | 1.25-37V [91] | 1.25-37V [94] | 1.25-37V [92] | 1.25-37V [93] | 1.22-32V [95]
Switching Frequency | 52 kHz | 52 kHz | 150 kHz | 260 kHz | 500 kHz
General Efficiency | 75-88% | 75-88% | 73-90% | 82-92% | 95%(maximum)

## Slide 26: 03 Schematics & PCB Layouts

## Slide 27: Main Board – HV Measurement

## Slide 28: Main Board – Input/Output

## Slide 29: Main Board – MCU & Programmer

## Slide 30: Regulator Boards- 3.3V

## Slide 31: Regulator Boards- 5V

## Slide 32: User Interface Board

## Slide 33: Test Bank Board

## Slide 34: 04 Software Design

## Slide 35: Interaction Flowchart
Maintain Safe Voltage
Adjust Setpoint
Discharge Sequence
Power On
Display Warning
Setup Menu

## Slide 36: Interaction Flowchart
Maintain Safe Voltage
Adjust Setpoint
Discharge Sequence
Power On
Display Warning
Setup Menu

## Slide 37: Program Phases & States

## Slide 38: Configuration Phase
Select 2nd Stage Option
Modifies Stage 2 starting voltage when selected
Adjust 2nd Stage Threshold
Keeps value within volt range
Adjust 3rd Stage Threshold
Keeps value within volt range
Select 3rd Stage Option
Modifies Stage 3 starting voltage when selected
Reset Default Values
Input Adjustments
Start Discharge Sequence

## Slide 39
Reset Default Values
Start Discharge Sequence
Select 2nd Stage Option
Modifies Stage 2 starting voltage when selected
Adjust 2nd Stage Threshold
Keeps value within volt range
Adjust 3rd Stage Threshold
Keeps value within volt range
Select 3rd Stage Option
Modifies Stage 3 starting voltage when selected
Select
Up/Down
Clears customizations when selected
Using provided setpoints for each Stage

## Slide 40: Discharge Phase
1st Stage
2nd Stage
3rd Stage

## Slide 41
User Cancel
(back to menu)
Open all
Contactors
(to Unsafe Condition)
Select Button
Next Setpoint
1st Stage
2nd Stage
3rd Stage
Close First Contactor
Turn On Stage 1 LED
Keep Stage 1 Contactor and LED Enabled
Power Stage 2 Contactor and LED
Hold all 3 Contactors
Show Stage 3 LED
Unsafe State

## Slide 42: Completion Phase
Safely Discharged
Unsafe Condition

## Slide 43
Safely Discharged
Unsafe Condition
Select to Reset
Stage 3 drops below 10V
Any Unsafe State

## Slide 44: 05 Prototyping & Testing

## Slide 45
Chart: LTSpice Simulation Voltage vs. Time Colored by Discharge Phase

## Slide 46: State Simulation

## Slide 47: RTD Testing
Initialized and read temperature data from the MAX RTD-to-Digital converter

## Slide 48: Display Testing
Initialized and displayed graphics on the screen / simultaneous testing with RTD

## Slide 49: 06 Future Plans

## Slide 50: Manufacturing Plan
Discharge plate material currently in UCF Machine Shop
Future Machining of Acrylic Still Needed
PCBs have been manufactured by JLCPCB and are en route
Task | Date completed/ongoing
PCBs Delivered to Team | 2/12
All PCBs Assembled | 2/20
Discharge Plate Manufactured | 2/20
Assembled PCB Testing | 2/23 to 2/27
Discharge Plate Assembled | 2/27
Integration Testing | 3/2 to 3/6
Midterm Demo Submission | 3/7
Acrylic Manufactured | 3/13
Full System Assembly | 3/20
Continued Testing & Potential Repairs | 3/23 to 3/27
Final Demo Dates | 4/20 to 4/23
Notes: Check dates/table (Done)

## Slide 51: Potential High Voltage Test
Prototype requirement for low voltage (12 V input)
NextEra long term goal for high voltage (1200 V input)
Testing potentially available for high voltage (Dr Weeks)
Calculations and design for both high and low voltage

## Slide 52: Budget Update
1833 total after tax lines up with prior estimates.
Type | Cost($)
Discharge Chassis | 797.44
Main PCB | 187.24
Test Bank | 7.28
Power Supply | 94.44
Regulators | 36.22
Manufacturing | 700.00
Total | 1833.78

## Slide 53: Thanks!